System luminaires / Downlights / SN 8500

SN 8500-08 SHB LED J/SV IP65,HWF 9006 - (101302453)

Safety luminaire SN 8500-08 SHB LED J/SV  HWF 9006

Downlight for enhanced lighting requirements. For illuminating large areas with high mounting heights. Robust, chlorine-resistant housing made of die-cast aluminium with optional lateral cable gland.

Ball-impact and shock resistant safety luminaires tested acc. to DIN VDE 0710-13.

Luminaires without testing acc. to DIN VDE 0710-13 as well as luminaires wih ball impact guards are not approved. According test certificates need to be added to the offer.

Light distribution: Symmetric High Bay, Symmetric Low Bay, for the illumination of areas. For mounting heights up to: 24,0 m. maximum 23,6 m luminaire distance for area illumination with 1 lx according to EN 1838, taking into account a maintenance factor of 0.8.

Incl. 4-chip LED illuminant for maximum safety. 

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. LED output dimmable continuously in mains operation. For connection to JOKER-central battery systems.

- Mounting type: ceiling mounting
- Material: die-cast aluminum
- Dim.: Length x Width x Height: 173 mm x 328 mm x 72 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 1 x 8W LED-module
- Light colour: 4000 K
- Light distribution: Symmetric High Bay, Symmetric Low Bay
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP65
- Protection class: I
- Impact resistance: IK10
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 49 mA
- Apparent power: 12,5 VA
- Inrush current: 8 A / 50 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.