System luminaires / Aluminium luminaires / SNP 7235

SNP 7235 D LED J/SV - (101955383)

Escape sign luminaire SNP 7235D LED J/SV  Aluminium

Double-sided exit sign luminaire made of high-quality aluminum profile. Especially flat design and an efficient and homogeneous illumination of the pictogram, using modern light guide technology. For easy and flexible installation, the cable entry is possible from the rear and from the side.

The following characteristics need to be complied with:

LED-driver with integrated individual lamp monitoring for stand-by and continuous lighting without seperate BUS-line. Complying with international standards for safety and working, electromagnetic compatibility and interference resistance. LED output dimmable continuously in mains operation. For connection to JOKER-central battery systems.

- viewing distance: 35 m

- Mounting type: ceiling mounting
- Material: aluminium
- Dim.: Length x Width x Height: 348 mm x 217 mm x 50 mm
- Input terminal: max. 2.5 mm² single-core or max. 1.5mm² multi-core with ferrule

- Illuminant: 18 x 0,1W LED-module
- Light colour: 6500 K
- Service life: 50.000 h
- Dimming: in mains operation logarithmically 10% steps

- Monitoring type: Individual luminaire monitoring with detailed clear text- / location

- Protection category: IP40
- Protection class: II
- Rated voltage: 230 V AC/DC +/-10 % 50/60 Hz; DC: 176 V - 264 V
- Power consumption battery operation: 17 mA
- Apparent power: 4,9 VA
- Inrush current: 6 A / 98 µs
- Permitted temperature range: -15...+40 °C

5-year manufacturer's warranty on INOTEC brand products.

Made in Germany

Version of the luminaire named above acc. to DIN VDE V 0108-100-1, IEC 60598-1, IEC 60598-2-22, DIN 4844 and EN 1838. EMC protection acc. To EN 550 15.

LED driver according to  EN 61000-3-2, EN 61347-1, EN 61347 2-13 and EN 61547.

An CE declaration of conformity for compliance with the Low Voltage Directive 2014/35/EC, RoHS Directive 2011/65/EU, electromagnetic compatibility 2014/30/EU and the above-mentioned standards must be documented. In addition, data sheets must be provided for documentation purposes.

When a different brand is offered, the equality of the characteristics needs to be recorded in written form and added to the offer. A lighting calculation needs to be demonstrated and added to the offer for safety lightings. Additional costs that occur due to the different brand are not refundable.

Brand: INOTEC Sicherheitstechnik GmbH
or equivalent and ready for use.

paror equivalent and ready for use.